1. PURPOSE

To establish a rigorous, standardized, and auditable procedure for reading utility meters that ensures:

- 100% accurate and repeatable readings

- Full traceability between recorded data and physical meters

- Elimination of human error, estimation, and manipulation

- Safe reading practices (especially for gas and electrical systems)

- Compliance with international standards and brand audits

2. SCOPE

This procedure applies strictly to meter reading activities only for all utility meters in the facility:

2.1 Water

- Main incoming water meter

- Dyeing machines

- Boilers

- Cooling systems

- ETP (inlet & outlet)

- DOMESTIC WATER

2.2 Electricity

- Main incomer

- Submeters (spinning, knitting, dyeing, printing, garment)

- Compressors

- HVAC systems

- Lighting panels

2.3 Natural Gas

- Main gas meter

- Boiler gas consumption meters

- Submeters (if available)

3. COMPLIANCE FRAMEWORK

This procedure ensures compliance with:

- Higg Facility Environmental Module (accurate tracking & verification)

- ISO 14001 Clause 9.1 (Monitoring & Measurement)

- Global brand requirements

- GOTS & GRS

4. DEFINITIONS

- Meter Reading: Direct recording of displayed meter value without calculation

- Cumulative Meter: Meter with continuously increasing value

- Submeter: Meter assigned to a specific process

5. RESPONSIBILITIES

| Role | Detailed Responsibility |
| --- | --- |
| Operator | Perform readings, ensure accuracy, immediate recording |
| Supervisor | Verify readings, detect abnormalities |
| Maintenance | Ensure meters are functional, calibrated, accessible |
| SUSTAINABILITY DEPARTEMENT | Audit compliance and record integrity |

6. REQUIRED TOOLS, EQUIPMENT & PPE (MANDATORY)

6.1 Recording & Documentation Tools

- Approved Meter Reading Log Sheet (hard copy or tablet)

- Permanent pen (no pencil allowed)

- Calculator (for quick validation if needed)

- Mobile device (photo evidence – recommended for audit)

6.2 Inspection Tools

- Flashlight (for dark areas)

- Cleaning cloth (for display clarity)

6.3 Personal Protective Equipment (PPE)

General Areas:

- Safety shoes

- Gloves

Electrical Areas:

- Insulated gloves

- Arc-rated PPE (if required)

Gas Areas (CRITICAL):

- Portable gas detector

- Anti-static clothing

- Safety helmet

6.4 Access Equipment

- Approved ladder

- Access permit (if restricted area)

7. PRE-READING CONTROL CHECK (CRITICAL STEP)

Before reading ANY meter, operator must confirm:

7.1 Identification

- Correct Meter ID

- Correct location

- Correct resource (water/electricity/gas)

- Unit of measurement

7.2 Physical Condition

- Display readable

- No cracks or damage

- No signs of tampering

7.3 Safety Verification

Water:

- No leakage

Electricity:

- No exposed wires

- No alarm indicators

Gas:

- No gas odor

- No leakage sound

- Area ventilated

⚠️ If unsafe → STOP and report

8. STANDARD READING CONDITIONS

- Reading time must be fixed daily (e.g., 08:00 AM)

- Allowed variation: ±15 minutes

- Same sequence of meters daily

- Same operator preferred

9. STEP-BY-STEP METER READING PROCEDURE

Step 1: Safe Access

- Ensure safe approach

- Wear required PPE

- Use ladder if needed

Step 2: Clean & Prepare

- Clean meter display if dirty

- Ensure visibility

Step 3: Visual Inspection

Check:

- Display clarity

- No damage

- No leakage (water/gas)

- No abnormal vibration/noise

Step 4: Read Meter Value

Digital Meter:

- Record full value (including decimals if required)

Analog Meter:

- Record all digits left to right

- Ignore red/rotating dial unless required

Step 5: Immediate Recording (MANDATORY)

➡ Record reading immediately on-site
➡ No memorization allowed

Step 6: Recording Format

| Date | Time | Meter ID | Resource | Area | Previous Reading | Current Reading | Unit | Operator | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Step 7: On-Site Validation

Operator must check:

- Current ≥ Previous

- Logical increase

- No abnormal jump

If abnormal → note in remarks

10. RESOURCE-SPECIFIC INSTRUCTIONS

10.1 Water

- Unit: m³

- Check nearby leakage

- Ensure continuous increase

10.2 Electricity

- Unit: kWh

- Check display stability

- No error codes

10.3 Natural Gas (HIGH RISK)

Additional Safety Checks:

- No gas smell

- No leakage sound

- Stable pressure

Reading Rules:

- Unit: m³ or Nm³

- Record exact value (no rounding)

11. ERROR PREVENTION CONTROLS

Operators must avoid:

- Skipping meters

- Estimating values

- Recording from memory

- Wrong unit entry

- Digit misplacement

12. ABNORMAL READING PROTOCOL

Trigger Conditions

- Sudden increase (>10%)

- No change

- Unexpected decrease

Required Actions

- Re-check reading

- Confirm meter ID

- Inform supervisor immediately

- Record in remarks

- Do NOT modify data

13. RECORD CONTROL & INTEGRITY

- No overwriting allowed

- Corrections must:

  - Be crossed once

  - Signed by operator and supervisor

- Records must be:

  - Clear

  - Complete

  - Traceable

14. DOCUMENTATION REQUIREMENTS

Maintain:

- Daily reading sheets

- Signed verification records

- Meter register

- Photo evidence (optional but recommended)

15. INTERNAL AUDIT REQUIREMENTS

Auditors will verify:

- Daily readings without gaps

- Same reading time

- Consistency

- Inclusion of gas readings

- Traceability to physical meters

16. TRAINING REQUIREMENTS

All personnel must be trained on:

- Meter types and units

- Reading accuracy

- Safety (gas & electrical)

- Error prevention

17. NON-CONFORMITY MANAGEMENT

| Issue | Action |
| --- | --- |
| Missing reading | Immediate correction |
| Wrong data | Retraining |
| Unsafe reading | Stop work immediately |

18. APPROVAL

Prepared by: __________
Reviewed by: __________
Approved by: __________
Date: __________